| Customer: | LERAT |  |  |  | Legend: |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Customer Site: | INSTRUMEXPERT |  |  |  | formulas |  |  |  |  |  |  |  |  |  |  |  |  |
| Instrument Tag Number: | LRC2011 |  |  |  | pick list |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | data entry |  |  |  |  |  |  |  |  |  |  |  |  |
| Pressure and Level Measurement Using an IASPT DP Transmitter With Pressure Seal(s) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Determine calibrated range (for level) and estimate performance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | EGU | Distance | Temp. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Measurement Engineering Units | mbar | mm | Deg C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Measurement Range Data |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Application | Level, Closed Tank |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Liquid Level Span, X | 2650 | mm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Liquid Level Offset, Y | 0 | mm |  | Legend: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Vertical distance between seals, d, | 2650 | mm |  | formulas |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Nominal specific gravity of meas. Fluid, GL | 0.68 |  |  | pick list |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Specific gravity of seal fill fluid, GS | 0.9072 |  |  | data entry |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Process Temperature Range, deg C | High side | Low Side |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Maximum | 20 | 20 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Normal | 20 | 20 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Minimum | 20 | 20 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ambient Temperature Range, deg C | High side | Low Side |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Maximum | 40 | 40 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Normal (or temp. when xmtr is zeroed) | 10 | 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Minimum | -35 | -35 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Configuration |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | High side | Low Side | Seal Type and Size |  | pss_2a-1z11a_a.pdf |  |  |  |  | Dimensional Print |  |  |  |  |  |  |  |
| Capillary Length, ft | 0 | 25 | High side | PSFLT-.3, Flush 3" direct conn. Flange mount seal |  |  |  |  |  | dp_020-342_b.pdf |  |  |  |  |  |  |  |
| Fill Fluid | DC200, 3CST |  | PIC W35FF, Flush Mount seal for 3" flange connection, direct connected to IDP10, IGP20 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Capillary Internal Diameter, inches | 0.027 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Transmitter | IDP10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Span Code | D |  |  |  |  |  |  |  |  | Dimensional Print |  |  |  |  |  |  |  |
|  |  |  | Low side | PSFPS-.3, 3" Flush mount (pancake) remote seal |  |  |  |  |  | dp_020-343_b.pdf |  |  |  |  |  |  |  |
|  |  |  | PIC W35FP, Flush Pancake (paddle) seal for 3" flange connection. Previously known as the MP type seal. Best price/performance selection. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Results Below |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The minimum process pressure must be above the fill fluids vapor pressure at the maximum temperature. | Fluid Vapor pressure @ max. temp. |  |  |  |  |  | Legend: |  | Linls to Dimensional Prints |  |  |  |  |  |  |  |  |
|  | 0.03310 | mm Hg, abs. |  |  |  |  | formulas |  | dp_020-342_b.pdf |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | pick list |  | dp_020-343_b.pdf |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | data entry |  | dp_020-345_a.pdf |  |  |  |  |  |  |  |  |
|  | Calibrated Range: |  | 8400 |  | in H2O |  |  |  | dp_020-346_a.pdf |  |  |  |  |  |  |  |  |
| Notes: | HW @ min. level, or LRV, |  | mbar | -235.30434 | -94.648819 |  |  |  | dp_020-347_a.pdf |  |  |  |  |  |  |  |  |
| Estimates are for 316ss diaphragms - other materials may have ambient and process temp. errors as much as 3X greater. | HW @ max. level, or URV, |  | mbar | -58.929835 | -23.703937 |  |  |  | dp_020-348_a.pdf |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | dp_020-349_a.pdf |  |  |  |  |  |  |  |  |
|  | Performance Estimates: |  |  |  |  |  |  |  | dp_020-350_a.pdf |  |  |  |  |  |  |  |  |
|  | Temperature effects from normal process and ambient temperatues |  |  |  |  |  |  |  | dp_020-351_a.pdf |  |  |  |  |  |  |  |  |
|  | to the respective maximum and minimum temperatures. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Process Temp. Effect |  | Ambient Temp. Effect |  | Head Effect for GS |  | Total Seal SystemTemp. Effect |  | Tolerance of Estimate* |  |  |  |  |  |  |  |  |
|  | for given temp. range |  | for given temp. range |  | chg. over distance d |  |  |  |  |  |  |  |  |  |  |  |  |
|  | mbar | % of Span | mbar | % of Span | mbar | % of Span | mbar | % of Span | +/- | mbar |  |  |  |  |  |  |  |
| To Max. Temp | 0.00 | 0.00 | -0.87 | -0.49 | 8.40 | 4.76 | 7.53 | 4.27 | 0.24 |  |  |  |  |  |  |  |  |
| To Min. Temp | 0.00 | 0.00 | 1.30 | 0.74 | -12.61 | -7.15 | -11.30 | -6.41 | 0.35 |  |  |  |  |  |  |  |  |
|  | * Tolarance for process and ambient temp. effects due to residual variation in seal characteristics. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Response Time Estimates: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Response values are calculated using nominal values for capillary ID and fluid viscosity. Actual times could be as much as 2 X greater or 1/2 X less than shown because of tolerances for capillary ID & viscosity | Ambient Temp, deg C |  |  | -35 | 10 | 40 |  |  |  |  |  |  |  |  |  |  |  |
|  | 90% response time, seconds |  |  | 0.31 | 0.09 | 0.05 |  |  |  |  |  |  |  |  |  |  |  |
|  | Time constant, seconds |  |  | 0.13 | 0.04 | 0.02 |  |  |  |  |  |  |  |  |  |  |  |